SIXTH FRAMEWORK PROGRAMME NETWORK OF EXCELLENCE

Safety of Hydrogen as an Energy Carrier

Contract No SES6-CT-2004-502630

Classification of Hazardous Zones – methodology and examples

Deliverable D64 (WP 12)

Lead participant:	DNV

Report prepared by Sandra Nilsen, (Hydro), Angunn Engebø (DNV), Alessia Marangon (UNIPI), Marco Carcassi (UNIPI), Jacques Chaineaux (INERIS), Iñaki Azkarate and Estibaliz Ezponda (Inasmet), Prankul Middha (Gexcon), Alexander Venetsanos (NCSRD), Christian Kirchensteiger, (JRC), Frank Markert (Risø), Mike Wardman (HSE/HSL), Frederic Barth (Air Liquide)

Dissemination level:	PP

Document version:	1.0

Date of preparation:	December 2006

# APPENDIX 1 – Detailed presentation of the Italian methodology

# APPENDIX 2 – Description of generic hydrogen station

# APPENDIX 4 – Detailed calculations (Alessia, Sandra, Prankul, Alexander , more?)

## Detailed calculation of the results obtained with the Italian Method (Guide 31-35 and Guide 31-35/A):

Definition of the hazardous substance.

| Substance | Hydrogen |
| --- | --- |
| Density, (gas (T=20 °C and p=101325 Pa) | 0.0772 kg/m3 |
| Molar mass, M | 16.34 kg/kmol |
| Ratio between specific heat at constant pressure and specific heat at constant volume, (=Cp/Cv | 1.41 |
| LEL | 4,0 vol.%; 0.003355 kg/m3 |

Scenario 1– Valve leak inside the dispenser enclosure

Definition of the environment and components.

| Location | Dispenser enclosure. All the valve and connections are located inside the enclosure (confined environment) with natural ventilation. |
| --- | --- |
| Box volume | Total free volume: 1,2 m3 TO BE VERIFIED |
| Ventilation | Natural ventilation through openings |
| Openings | 4 ventilation openings, each with dimensions of 0,08 * 2 m2 TO BE VERIFIED |
| Operating pressure, P | 460 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 2 or 3 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

The natural ventilation is due to the wind that enters the local through the openings; the natural ventilation flow rate, Qa, is evaluated as:

(1)

(2)

where:

Aw =	opening’s area coefficient = 0,226 m2 (Ahigh: total area of the openings located in the high part of the box = 0,32 m2; Alow: total area of the openings located in the bottom part of the box = 0,32 m2) TO BE VERIFIED

w =	wind’s speed outside the confined environment = 0,5 m/s

(cp =	0.9 ( 0.1; it is the coefficient that takes into account the wind speed prevalent direction with respect to the openings ((cp = 0.9 when the wind prevalent direction is perpendicular to the openings; (cp = 0.4 when the wind prevalent direction is at 45° with respect to openings; (cp = 0.2 when the wind prevalent direction is <45° with respect to openings; (cp = 0.1 when the openings are shielded by other structures or obstacles). In the present case it is assumed (cp = 0.9, however it would be cautelative to apply some reduction factor due to protection structures on the openings (grates).

The number of air changes inside the free volume of the box is evaluated as:

(3)

where Va is the internal free volume of the box = 1,2 m3.

CONTINUOUS GRADE EMISSION IN THE CONFINED ENVIRONMENT

Inside the enclosure it is supposed that there are:

- 3 flange connections

- 3 valves

The continuous grade emissions could be contemporary as they are leaks from discontinuity points. The Italian Guide gives these reference parameters to apply for the evaluation of the emission flow rates:

| Qg flange [kg/s] | Qg valves[kg/s] |
| --- | --- |
| 1,9 10-8 | 5,6 10-7 |

Evaluation of the Zone extension:

(4)

= 0,0322509804    %vol.		(5)

=  1,22						(6)

NOTE: if the medium concentration of the explosive atmosphere in the confined environment, Xm%vol. is smaller than k LEL%vol. then the explosive atmosphere is not extended to the whole volume of the confined environment. In this case the extension of the hazardous zone is equal to dz around the sources of emissions.

So it should be verified the following relation:

(7)

In the present case it results:

| Xm %vol. | < | K*LEL%VOL/f |
| --- | --- | --- |
| 0,0322509804 |  | 0,3333333333 |

So the hazardous area due to the continuous grade emission is not extended to the whole internal volume of the enclosure.

Determination of the hazardous volumes generated by the leaks:

(8)

| Vz flange [m3] | Vz valves [m3] |
| --- | --- |
| 0,0000068309 | 0,0012945049 |

Both the hazardous volume generated by the flange and the valve leaks are negligible, so the ventilation grade should be considered HIGH. The type of the hazardous areas is determined entering the table on the influence of ventilation on type of zone of the EU Norm 60079-10 (the same of the Italian method) with the combination of the following conditions:

- Continuous grade of emission;

- Availability of the ventilation GOOD (natural ventilation has always a good availability when it refers to a wind velocity of 0,5 m/s, a very conservative value);

- Ventilation grade HIGH

The hazardous area is ZONE 0 NE (Non hazardous).

This means that the continuous grade emissions don’t generate hazardous areas.

SECONDARY GRADE EMISSION IN THE CONFINED ENVIRONMENT

The secondary emissions are not expected to occur in normal operation and, if it does occur, is likely to do so only infrequently and for short period. The secondary emission are not expected to be contemporary, so the worst scenario should be evaluate when assessing an hazardous area. In this case it is the fault of a valve located inside the enclosure.

Several values of leak size have been considered:

- 0,25 mm2: proposed value of leak size in the Guide 31-35 and 31-35/A (this values don’t refer to hydrogen, but to industrial installation of natural gas / methane probably with larger equipment dimensions and lower process pressure than for the current HRS technology). To examine the effect of reduced, and probably more realistic release sizes it has been decided that for all scenarios a leak size with leak diameter 0.1 mm and 0.2 mm will be considered for secondary grade of  releases.  This corresponds respectively to release areas of:

- 0,03 mm2

- 0,008 mm2

The emission flow rate from a hole can be sonic or sub-sonic. The type of the flux is evaluated through the verification of the following relation:

if   		then the flux is sonic					(9)

as   0.002 ≤ 0.54		then the flux is sonic

Where:

Pa:	101325 Pa, atmospheric pressure

P:	190 105 Pa (190 bar): absolute pressure within the piping

(:	1.31, ratio between specific heat at constant pressure and specific heat at constant volume.

The emission flow rate is expressed as:

[kg/s]				(10)

Where:

(:	1	in the case of sonic flux

c:	0.8	emission coefficient

(:	= 7.45

R0:	8314 J/kmol K: universal constant of gas

So:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Qg [kg/s] | 5,69 10-3 kg/s | 6,83 10-4 kg/s | 1,82 10-4 kg/s |

When evaluating the medium concentration of the explosive atmosphere in the confined environment Xm %vol., due to the secondary grade emission, also the continuous grade emissions should be taken into account, as they might occur contemporarily. The gas concentration in air, due to the secondary grade emissions, rises in an exponential way depending on the free volume of the environment. The medium volume concentration, Xte%, after the emission time “te” is estimated as:

[%vol.]				(11)

vol.       (12)

Where:

te:	300 s, time of emission plus the time needed for the operator to intervene.

As already seen with equation (7), if the medium concentration of the explosive atmosphere in the confined environment, Xm%vol. is smaller than k LEL%vol. then the explosive atmosphere is not extended to the whole volume of the confined environment.

Since this relation is not verified (for all the three hole sizes), the flammable atmosphere should be considered extended to the whole internal volume of the enclosure, and the grade of ventilation should be considered “Low” (LV).

The type of the hazardous areas is determined entering the table on the influence of ventilation on type of zone of the EU Norm 60079-10 (the same of the Italian method) with the combination of the following conditions:

- Secondary grade of emission;

- Availability of the ventilation GOOD (natural ventilation has always a good availability when it refers to a wind velocity of 0,5 m/s, a very conservative value);

- Ventilation grade LOW

The hazardous area is ZONE 1 extended to all the internal volume of the dispenser enclosure.

CLASSIFICATION OF THE AREA OUTIDE THE OPENINGS OF THE DISPENSER ENCLOSURE

The openings constitute emission sources as the internal atmosphere is flammable.

According to the Italian guides 31-35 and 31-35/A the fixed ventilation outlets are openings of Type A, so they generate an emission of primary grade (see the following table extracted from the Italian guides).

Openings classification

| Zone upstream the opening | Opening type | Grade of release of the opening |
| --- | --- | --- |
| Zone 0 | A | Continuous |
|  | B | (Continuous) 1) / Primary |
|  | C | Secondary |
|  | D | No release |
| Zone 1 | A | Primary |
|  | B | (Primary) 1) / Secondary |
|  | C | (Secondary) 1) / No release |
|  | D | No release |
| Zone 2 | A | Secondary |
|  | B | (Secondary) 1) / No release |
|  | C | No release |
|  | D | No release |

1) For grade of release shown in brackets, the frequency of operation of the openings should be considered

For safety reasons, the gas flow rate at the openings is assumed equal to the gas flow rate from the valve that generate the hazardous Zone 1. Evaluating the extension of the hazardous area for a release at atmospheric pressure:

(13)

these are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| dz [m] | 0,5 m | 0,2 m | 0,1 m |

The hazardous volume, Vz, is evaluated through:

(14)

these are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Vz [m3] | 0,028 m3 | 0,0011 m3 | 0,00016 m3 |

- In the case of the valve’s hole size inside the enclosure of 0,25 mm2, the openings generate a Zone 1 (result obtained entering the table on the influence of ventilation on type of zone of the EU Norm 60079-10 (the same of the Italian method) with the combination of the following conditions: Primary grade of emission; Availability of the ventilation GOOD; Ventilation grade MEDIUM). The Zone 1 is hemispherical with a radius of 0,5 m.

- In the case of the valve’s hole size inside the enclosure of 0,03 and 0,008 mm2, the openings generate a Zone 1 NE (result obtained entering the table on the influence of ventilation on type of zone of the EU Norm 60079-10 (the same of the Italian method) with the combination of the following conditions: Primary grade of emission; Availability of the ventilation GOOD; Ventilation grade HIGH). But for safety reason it is suggested a Zone 1 hemispherical with a radius of 0,2 m and 0,1 (leak hole size of 0,03 and 0,008 mm2respectively.

Scenario 2– Opening of safety valve – release from release point

Definition of the environment and components.

| Location | Vent line for the safety valve. Open environment. 4 m above ground. See Figure 1 |
| --- | --- |
| Ventilation | Natural ventilation |
| Operating pressure, P | 460 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 1 |
| Release diameters, A | 0,25 mm2 TO BE VERIFIED. THE OPENING AREA OF A SAFETY VALVE SHOULD BE FIXED. |

SECONDARY GRADE EMISSION IN OPEN  ENVIRONMENT

The flux is sonic (see equation (9), P=460 barg).

The emission flow rate Qg = 5,51 10-3 kg/s is evaluated through equation (10).

The extension of the hazardous area, dz = 5 m is evaluated through equation (13). Since the release from a safety valve is well oriented upwards (pressure driving force), for safety reason it is better to extend the hazardous areas upwards.

So the classified area should be of the shape of a cone with the vertex in the discharge point of the valve. Height of the cone 7,5 m and base radius of 5,0 m for the safety level of 2 %vol. Hydrogen in air.

The hazardous volume, Vz = 71,55 m3,  needed to evaluate the degree of ventilation is calculated through equation (14).

The type of the area, Zone 2, is evaluated entering the table on the influence of ventilation on type of zone of the EU Norm 60079-10 (the same of the Italian method) with the combination of the following conditions: Secondary grade of emission; Availability of the ventilation GOOD; Ventilation grade MEDIUM.

So for the scenario of opening of safety valve of the vent line the suggestion is to settle a Zone 2 with the shape of a cone with the vertex in the discharge point of the valve. Height of the cone 7,5 m and base radius of 5,0 m for the safety level of 2 %vol. Hydrogen in air.

Scenario 3– Outdoor valves at storage vessels

Definition of the environment and components.

| Location | Outdoor valves at storage vessels. Open environment. 1 m above ground. See Figure 1 |
| --- | --- |
| Ventilation | Natural ventilation |
| Operating pressure, P | 460 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 1 or 2 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

For the formulas applied see “Scenario 2 - Opening of safety valve – release from release point” as the leak takes place in open environment as well.

These are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Type of Zone | Zone 2 | Zone 2 | Zone 2 |
| dz [m] | 5 m | 1,7 m | 1,0 m |
| Shape | Spherical | Spherical | Spherical |

Scenario 4– Refuelling nozzle

Definition of the environment and components.

| Location | Outdoor, refuelling nozzle. Open environment. 1 m above ground. See Figure 1 |
| --- | --- |
| Ventilation | Natural ventilation |
| Operating pressure, P | 460 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 1 or 2 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

For the formulas applied see “Scenario 2 - Opening of safety valve – release from release point” as the leak takes place in open environment as well.

These are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Type of Zone | Zone 2 | Zone 2 | Zone 2 |
| dz [m] | 5 m | 1,7 m | 1,0 m |
| Shape | Spherical | Spherical | Spherical |

Scenario 5– Valve at buffer tank

Definition of the environment and components.

| Location | Outdoor, valve at buffer tank. Open environment. 1 m above ground. See Figure 1 |
| --- | --- |
| Ventilation | Natural ventilation |
| Operating pressure, P | 15 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 1 or 2 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

For the formulas applied see “Scenario 2 - Opening of safety valve – release from release point” as the leak takes place in open environment as well.

These are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Type of Zone | Zone 2 | Zone 2 | Zone 2 |
| dz [m] | 0,90 m | 0,35 m | 0,20 m |
| Shape | Spherical | Spherical | Spherical |

Scenario 6– Shutoff valve outside gas processing building

Definition of the environment and components.

| Location | Outdoor, Shutoff valve outside gas processing house. Open environment. 1 m above ground. See Figure 1 |
| --- | --- |
| Ventilation | Natural ventilation |
| Operating pressure, P | 460 barg |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s |
| Ventilation efficiency, f | f = 1 or 2 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

For the formulas applied see “Scenario 2 - Opening of safety valve – release from release point” as the leak takes place in open environment as well.

These are the results:

|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| --- | --- | --- | --- |
| Type of Zone | Zone 2 | Zone 2 | Zone 2 |
| dz [m] | 5,0 m | 1,70 m | 1,00 m |
| Shape | Spherical | Spherical | Spherical |

Scenario 7– Release inside the gas processing building

Definition of the environment and components.

| Location | Indoor, shutoff valve outside gas processing house. Confined environment. See Figure 2 |
| --- | --- |
| Ventilation | Natural ventilation and forced ventilation |
| Operating pressure, P | 15 barg at the inlet and 460 barg at the outlet |
| Ambient pressure, Pa | 1 atm |
| Operating temperature, Ta | 25 °C |
| Wind velocity, w | 0,5 m/s in natural ventilation |
| Ventilation efficiency, f | f = 2 or 3 |
| Release diameters, A | 0,25 – 0,03 – 0,008 mm2 |

Inside the gas processing house it is supposed that there are:

- 1 compressor skid;

- 18 valves (assumption made on the basis of the document “Description of Generic refuelling station.doc” compiled by Sandra Nilsen and distributed between WP12 partners). DATA TO BE VERIFIED????

- 7 instrumentation valves (assumption made on the basis of the document “Description of Generic refuelling station.doc” compiled by Sandra Nilsen and distributed between WP12 partners). DATA TO BE VERIFIED????

- 3 safety valves (assumption made on the basis of the document “Description of Generic refuelling station.doc” compiled by Sandra Nilsen and distributed between WP12 partners). DATA TO BE VERIFIED????

For the formulas applied see “Scenario 1 - Valve leak inside the dispenser enclosure” as the leak takes place in confined environment as well.

When evaluating the case of forced ventilation note that the air changes per hour are fixed by the mechanical system (100, 300 and 800 air changes per hour).

These are the results:

| Natural ventilation |
| --- |
| Hazardous area classification | Release area |
|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| Inside the gas processing house | Type of Zone | Zone 0 | Zone 0 | Zone 0 |
|  | dz [m] | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building |
|  | Shape | / | / | / |
| Outside the ventilation openings | Type of Zone | Zone 0 | Zone 0 | Zone 0 |
|  | dz [m] | 0,5 m | 0,2 m | 0,1 m |
|  | Shape | hemisphere | hemisphere | hemisphere |
| Forced ventilation characterized by 150 air changes per hour |
| Hazardous area classification | Release area |
|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| Inside the gas processing house | Type of Zone | Zone 1 | Zone2 | Zone 2 |
|  | dz [m] | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building |
|  | Shape | / | / | / |
| Outside the ventilation openings | Type of Zone | Zone 1 | Zone 2 | Zone 2 |
|  | dz [m] | 1,2 m | 0,4 m | 0,2 m |
|  | Shape | hemisphere | hemisphere | hemisphere |
| Forced ventilation characterized by 300 air changes per hour |
| Hazardous area classification | Release area |
|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| Inside the gas processing house | Type of Zone | Zone 2 | Zone 2 | Zone 2 |
|  | dz [m] | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building | 1,8 m |
|  | Shape | / | / | Spherical |
| Outside the ventilation openings | Type of Zone | Zone 2 | Zone 2 | Zone 2 |
|  | dz [m] | 0,8 m | 0,3 m | 0,15 m |
|  | Shape | hemisphere | hemisphere | hemisphere |
| Forced ventilation characterized by 800 air changes per hour |
| Hazardous area classification | Release area |
|  | A = 0,25 mm2 | A = 0,03 mm2 | A = 0,008 mm2 |
| Inside the gas processing house | Type of Zone | Zone 2 | Zone 2 | Zone 2 |
|  | dz [m] | Extended to the whole internal volume of the building | Extended to the whole internal volume of the building | 1,8 m |
|  | Shape | / | / | Spherical |
| Outside the ventilation openings | Type of Zone | Zone 2 | Zone 2 | Zone 2 |
|  | dz [m] | 0,6 m | 0,2 m | 0,1 m |
|  | Shape | hemisphere | hemisphere | hemisphere |

# Text boxes

Classification of hazardous zones from openings in confined environments

Classification of hazardous zones for confined environment

Classification of hazardous zones for open environment